## Sheet1
METER APPLICATIONS/REQUIREMENTS
VOLTAGE | SERVICE AMPS | PHASE | CONFIGURATION | KW | FORM | SIEMENS-TALON | MILBANK | MIDWEST | ADDERS
120/240 | 100 - 200 | 1 | 3 WIRE DIRECT SOCKET | UNDER 50 | 2S | UAT417-XPQG② | U1773-XL-TG-KK②
[6 empty] | 40404-025① | U4801-XL①
120/240 | 100 - 200 | 1 | DOUBLE 200 AMP | UNDER 50 | 2S | UA2717YPZ② | U1252-X-KK-K1②
Eaton Catalog No. 1008842-CH (UHTT-2R2332U) - Not Approved
120/240 | 100 - 200 | 1 | 3 WIRE RESIDENTIAL PED | UNDER 50 | 2S | UAP317-PPWI② | U3358-O-KK②
120/240 | 320 | 1 | 3 WIRE DIRECT SOCKET | UNDER 50 | 2SE | 9804-8715① | U1797-O-K3L-K2L① |  | Anti-Inversion Kit required
120/240 | 320 (RINGLESS) | 1 | 3 WIRE RESIDENTIAL PED | UNDER 50 | 2SE | 47604P-9WI① | U1748-0-WI① |  | K1350/K4802--Siemens #H59676
120/240 | 100 - 200 | 1 | 3 WIRE DIRECT PEDESTAL | UNDER 50 | 2S | UAP317-PPWI② | U4322-0-5T9① |  | Milbank - Main Breaker Required
U5925-0-200-KK②
120/240 | 100-200 | 1 | 3 WIRE PEDESTAL W/ BREAKER | UNDER 50 | 2S |  |  | R281C1P6H034①
120/240 | 100-200 | 1 | 3 WIRE PEDESTAL W/ BREAKER | UNDER 50 | 2S |  | U5136-O-200S② | R208CP6HP②
120/240 | 100-200 | 1 | 3 WIRE SOCKET W/ BREAKER | UNDER 50 | 2S |  |  | R281C1P6H②
120/240 | 400 | 1 | 3 WIRE OVERHEAD 1 CT | UNDER 75 | 3S | UAT111-0MXA② | U7487-RL-TG-KK② |  | 5TH TERM (5T8K) - Must Bolt in
120/240 | 400 - 800 | 1 | 3 WIRE UG 2 CT | UNDER 75 | 4S | 9804-8544 or 9804-8548① | U4490-XL①
120/208 | 100- 200 | 3 | 4 WIRE WYE | UNDER 75 | 16S | 40407-025① | U9701-RXL①
277/480 | 100 - 200 | 3 | 4 WIRE WYE | UNDER 75 | 16S | 40407-025① | U9701-RXL①
277/480 | 200 | 3 | 4 WIRE WYE | 75-200 | 16S |  | U9107-0① |  | PED TYPE
120/208 | 200 | 3 | 4 WIRE WYE | 75-200 | 16S |  | U9107-0① |  | PED TYPE
120/208 | 400 - 800 | 3 | 4 WIRE WYE | 75-200 | 9S | 9804-8543 or 9804-8547① | U4493-XL①
277/480 | 200 - 400 | 3 | 4 WIRE WYE | 75-200 | 9S | 9804-8543 or 9804-8547① | U4493-XL①
120/208 | 1000 & UP | 3 | 4 WIRE WYE | 225 & UP | 9S | 9804-8543 or 9804-8547① | U4493-XL①
277/480 | 600 & UP | 3 | 4 WIRE WYE | 225 & UP | 9S | 9804-8543 or 9804-8547① | U4493-XL①
① Indicates Lever Bypass
② Indicates Horn Bypass
*** SOCKETS NOT LISTED, CALL OAKDALE FOR APPROVAL ***
*** ANY SERVICE REQUIRING A CT CABINET, MUST FURNISH THE LUGS ***
*** CT CABINETS OVER 1000 AMP, MUST SUPPLY THE BUSS ***
*** OAKDALE ELECTRIC APPROVED CT CABINETS (ALONG W/ MILBANK SOCKET # U4490-XL) ***
|  |  | 1) | GALVA CLOSURE OAK-634
|  |  | 2) | AMP ALICT6-3
*** ALL RESIDENTIAL METER SOCKETS MUST HAVE EITHER HORN OR LEVER BYPASS ***